## Sheet1
EUCEE & ASSOCIATES
SPECIFICATION FOR ELECTRICAL WIRING & DATA CABLING WORK FOR BARODA UP BANK AT PIPRAICH BRANCH, GORAKHPUR.
S.No. | Description of Items | Qty. | Unit | Rate | Amount
1- | ELECTRICAL PANEL: Design manufacture providig storing and installing in position affecting proper connection testing and commissioning of Panel made 14 SWG CRCA steel sheet. It shall be dust and vermin proof. It shall have compartmentalize construct on with Bus Bar chambers cable alloy, cable gland plates etc as required, duly painted by inside as well as outside. It shall have the following: (A) Incoming 1 no. 125 amp 4 pole MCCB (B) Bus Bar 150 amp 3 phase 4 stripes 415 volt 50 Hz copper bus bar with color coated PVC heat shrinkable sleeves, instrument with three phase indicator (C) Multifunctional metres for voltage ammetre power factor KWH data (D) Outgoing 4 nos. 63 Amp 4 pole MCCB for UPS , AC, Light , Fan etc. (E) 1 No. 100 amp off load changeover switch front handle in panel. | 1 | Set.
2- | Fuse Grip (Cut-out): Supply & Fixing of Kit-Kat Fuse Unit 100Amp three phase and Neutral set. | 1 | Set.
3- | Supply & Fixing of SPN MCB DB 12way Double Door with 40Amp DP RCCB 300ma for Light/Fan, UPS & Power. | 5 | Nos.
4- | Supply & Drawing Circuit line by (2x6+1x4.0)Sq.mm FRLS Copper Wire for Mains Connections. | 42 | Mtr.
5- | Supply & Drawing Circuit line by (2x4+1x2.5)Sq.mm FRLS Copper Wire for UPS, SPNDB & AC wiring | 240 | Mtr.
6- | Supply & Drawing Circuit line by (2x2.5+1x1)Sq.mm FRLS Copper Wire for All Circuit wiring. | 150 | Mtr.
7- | Supply & Drawing Circuit line by (2x1.5+1x1)Sq.mm FRLS Copper Wire for PC Circuit wiring. | 210 | Mtr.
8- | Light Point: Wiring by 1.5 Sq.mm Copper wire with all accessories like Switch, Socket etc..(if needed) | 49 | Nos.
9- | Fan Point: Wiring by 1.5mm Sq.mm Copper wire with Electronic Regulator & Switch.( if needed) | 2 | Nos.
10- | Supply & Fixing for Raw Power 25Amp Socket with Switch and top for AC and raw power. | 3 | Nos.
11- | Supply & Fixing for PC Terminal Power Board 4way 6Amp Socket with Switch. | 8 | Nos.
12- | Supply & Fixing Power Box with 20Amp SPN MCB and including Power Top for Safe, AC & Stationary Circuit. | 6 | Nos.
13- | Supply & Laying 10Sq.mm Copper/GI Strip Wire for Earthing Circuit Earth Place to UPS & Main. | 60 | Mtr.
14- | Supply & Fixing Ceiling Fan 1200mm as per advice by Bank authority.(if needed) | 2 | Nos.
15- | Supply & Fixing LED Batten Fitting 20Watt as per advice by Bank authority. | 4 | Nos.
16- | Re-Fixing Old Fans & Lights as per advice by Bank authority & Main Electrical Panel, Light, Fan other wiring dismatling | 1 | Job
|  |  |  | Contd-2 | 0

## Sheet2
EUCEE & ASSOCIATES
2
S.No. | Description of Items |  |  | Qty. | Unit | Rate | Amount
|  |  | B/F- Before Page--- |  |  | Rs.
17- | Supply & Drawing LAN Cabling by CAT-6 in PVC Conduit Pipe. |  |  | 210 | Mtr.
18- | Supply & Fixing Data 9U Rack as per advice by Bank Authority complete in all respects. |  |  | 1 | No.
19- | Supply & Fixing Networking Information Outlet Box with RJ-45 connector complete in all respects. |  |  | 6 | Nos.
20- | Earthing Work: Supply & Fixing Maintenance Free Pipe Earth 80mm with Backfil compound 40kg Bag resistance shuld be less than 2.0 Ohms specification as per IS 3043/1987 complete in all respects. |  |  | 2 | Nos.
21 | Supply & Fixing 40/32Amp DP MCB with Enclosure for UPS Incoming. |  |  | 1 | Set.
22- | Supply & Fixing 25Amp DP MCB with Enclosure for UPS Outgoing. |  |  | 1 | Set.
23- | 25 Amp Power Board for UPS in and out |  |  | 4 | Nos.
24- | S/F of Wall fan for Cash Cabin and Hall |  |  | 10 | Nos.
25- | S/F of Wall fan socket |  |  | 10 | Nos.
26- | S/F of Fan Down Rod and fasner hook |  |  | 2 | Nos.
27- | Supply and fixing of 2'x2' LED light 45 W |  |  | 10 | Nos.
28- | Supply and fixing of LED Round panel 12 W |  |  | 16 | Nos.
29- | P/F of main electrical Cable and generator cable |  |  | 50 | Mtr.
30- | S/F of Exhaust Fan 300 mm |  |  | 1 | Nos.
Total Rs.
List of Approved Make:-
Copper Wire FRLS Grade |  |  | : Finolex/ Polycab/ Havell's/ HCL/ Anchor/ RR Kable.
Electric Cable |  |  | : Havell's/ Polycab/ Kent/ SSK or Equivelent.
ELCB, MCCB & RCCB |  |  | : L&T/ Indo-asian/ Havell's/ ABB/ HPL/ Leagrand.
MCBs, DBs, SFUs |  |  | : L&T/ Indo-asian/ Havell's/ ABB/ HPL/ Leagrand.
Modular Switch, Sockets |  |  | : Anchor /Roma/ Crabtree/ MK/ Polycab/ Leagrand.
Earthing for Bldg. & UPS |  |  | : Earth Electrode IS:3043-1978 Chemical Earthing.
PVC Conduit Pipe |  |  | : AKG/ Precision/ Polycab/ Asian/ Fonolax.
Telephone & Data Cable |  |  | : D-link/ Finolex/ Polycab/ V-Gaurd/ HCL/ RR Kable.
Lugs |  |  | : Dowells/ Jainson or Equivelents.
Metal Clad Sockets |  |  | : HPL/ ABB/ Indo-asian or Equivelents.
Date: | 11.12.2024 | (U.C.SRIVASTAVA) |  | (Contractor's Seal & Sign)
Place: | GORAKHPUR | (Panel Architect)